## Intorduction
Peter L LaMontagne PE
Peter@TheCentrifugeGuys.com
Centrifuge Data Sheet
There are two active spreadsheets here, one is for centrifuges whose controls display the
The differential RPM ( also called the relative speed between the bowl and the conveyor),
the other is for centrifuges where the pinion speed is indicated. The pinion speed is the input.
speed to the gear box.
Enter you run data, and the spreadsheet will automatically calculate the polymer dose, the
wet and dry tons, and the overall capture.
In this spread sheet, the % load is the torque on the conveyor. Units can be, bar,
excitation, load, and amps. I prefer to express the load as % of allowed as otherwise the
operator must recall the makimum allowed torque, in order to appreciate how hig the torque level is.
These are the basic centrifuge process data sheets. I also have a spreadsheet that automatically
calculates the cost to dewater a ton of solids for each run. Call me for details.
Peter LaMontagne PE
190 N Tamenend Ave
New Britain, PA 18901 USA
Peter@TheCentrifugeGuys.com
215 348 7879

## Differential RPM
Peter L LaMontagne PE
Peter@TheCentrifugeGuys.com
Centrifuge Data Sheet (If your PLC displays the differential RPM)
| Plant Name |  |  | Marion Haste WWTP, NV
| Sludge |  |  | Anaerobically Digested
| Centrifuge |  |  | Centrifuges R/US 44/40 | [5 empty] | Polymer |  | Flockinggood #2
| SERIAL NO: |  |  | 93-SludgeChucker-147
| Poly addition point |  |  |  | 3' ahead of feed tube
Date | Run | Pond | Bowl |  | Differential | Feed | Feed | Eff. | Cake | Load | Wet | Dry | Poly | Poly | Poly | REC.
| No. | No. | Rpm |  | or | Rate | Conc. | Conc. | Conc | % | Cake | Cake | Conc. | Rate | Dose | %
[5 empty] | Relative | [5 empty] | Tons/hr | tons/hr | Active
[5 empty] | Rpm | GPM | %SS | %SS | %TS |  |  |  | % | GPM | #/TDS
2002-09-19 | 1 | 7.7 | 2800 |  | 3.3 | 120 | 2.4 | 0.19 | 21 | 25 | 3.1885 | 0.66959 | 0.2 | 10 | 20.8333 | 92.9241
| 2 | 7.7 | 2800 |  | 2.9 | 120 | 2.4 | 0.1 | 21.5 | 28 | 3.2269 | 0.69378 | 0.2 | 11 | 20.8333 | 96.2812
| 3 | 7.7 | 2800 |  | 2.7 | 120 | 2.3 | 0.07 | 23.5 | 35 | 2.8576 | 0.67154 | 0.2 | 13.5 | 21.7391 | 97.2462
| 4 | 7.7 | 2800 |  | 2.5 | 120 | 2.35 | 0.14 | 24.5 | 39 | 2.7239 | 0.66734 | 0.2 | 15 | 21.2766 | 94.583
| 5 | 7.7 | 2800 |  | 2.4 | 120 | 2.3 | 0.19 | 25.5 | 41 | 2.503 | 0.63826 | 0.2 | 17.5 | 21.7391 | 92.4278
| 6 | 7.7 | 2800 |  | 2.3 | 120 | 2.25 | 0.17 | 26 | 47 | 2.4177 | 0.62861 | 0.2 | 20 | 22.2222 | 93.0529
| 7 | 7.7 | 2800 |  | 1.9 | 120 | 2.3 | 0.08 | 26.3 | 55 | 2.5421 | 0.66857 | 0.2 | 21.5 | 21.7391 | 96.8162
| 8 | 7.7 | 2800 |  | 1.7 | 120 | 2.1 | 0.1 | 26.8 | 64 | 2.249 | 0.60273 | 0.2 | 25.1 | 23.8095 | 95.5948
Shaded colums are calculations the spread sheet makes

## Pinion RPM
Peter L LaMontagne PE
Peter@TheCentrifugeGuys.com
Centrifuge Data Sheet (If your PLC only displays the Pinion RPM)
| Plant Name |  |  | Marion Haste WWTP, Reno, NV
| Centrifuge |  |  | Centrifuges R/Us 44/40 |  |  |  |  | Polymer |  |  | Flockinggood #2
| SERIAL NO: |  |  | 93-SludgeChucker-147 |  |  |  |  | Poly addition point |  |  | 3' ahead of feed tube
| Bowl RPM |  |  | 2800 |  |  |  |  | Sludge |  |  | Anaerobically Digested
| Gear Box Ratio |  |  | 95
Date | Run | Pond | Pinion | Differential | Feed | Feed | Eff. | Cake | Load | Wet | Dry | Poly | Poly | Poly | REC.
| No. | No. | Rpm | or | Rate | Conc. | Conc. | Conc | % | Cake | Cake | Conc. | Rate | Dose | %
|  |  |  | Relative | [5 empty] | Tons/hr | tons/hr | Active
|  |  |  | RPM | GPM | %SS | %SS | %TS |  |  |  | % | GPM | #/TDS
2002-09-19 | 1 | 7.7 | 2487 | 3.2947 | 120 | 2.4 | 0.19 | 21 | 25 | 3.1885 | 0.66959 | 0.2 | 10 | 20.8333 | 92.9241
| 2 | 7.7 | 2525 | 2.8947 | 120 | 2.4 | 0.1 | 21.5 | 28 | 3.2269 | 0.69378 | 0.2 | 11 | 20.8333 | 96.2812
| 3 | 7.7 | 2544 | 2.6947 | 120 | 2.3 | 0.07 | 23.5 | 35 | 2.8576 | 0.67154 | 0.2 | 13.5 | 21.7391 | 97.2462
| 4 | 7.7 | 2563 | 2.4947 | 120 | 2.35 | 0.14 | 24.5 | 39 | 2.7239 | 0.66734 | 0.2 | 15 | 21.2766 | 94.583
| 5 | 7.7 | 2572 | 2.4 | 120 | 2.3 | 0.19 | 25.5 | 41 | 2.503 | 0.63826 | 0.2 | 17.5 | 21.7391 | 92.4278
| 6 | 7.7 | 2582 | 2.2947 | 120 | 2.25 | 0.17 | 26 | 47 | 2.4177 | 0.62861 | 0.2 | 20 | 22.2222 | 93.0529
| 7 | 7.7 | 2620 | 1.8947 | 120 | 2.3 | 0.08 | 26.3 | 55 | 2.5421 | 0.66857 | 0.2 | 21.5 | 21.7391 | 96.8162
| 8 | 7.7 | 2639 | 1.6947 | 120 | 2.1 | 0.1 | 26.8 | 64 | 2.249 | 0.60273 | 0.2 | 25.1 | 23.8095 | 95.5948
Shaded colums are calculations the spread sheet makes